108 Liberty St | Metuchen NJ 08840
800-422-1751 (t) | 732-452-0444 (f)
www.ushalonbank.com

MATERIAL SAFETY DATA SHEET

GREAT LAKES CHEMICAL -- 1,1,1,2,3,3,3-HEPTAFLUOROPROPANE, FM-200

NSN: 421000N078336

Manufacturer's CAGE: 2E394

Part No. Indicator: A

Part Number/Trade Name: 1,1,1,2,3,3,3-HEPTAFLUOROPROPANE, FM-200

===========================================================================

General Information

===========================================================================

Company's Name: GREAT LAKES CHEMICAL CORP

Company's Street: ONE GREAT LAKES BLVD

Company's P. O. Box: 2200

Company's City: WEST LAFAYETTE

Company's State: IN

Company's Country: US

Company's Zip Code: 47906

Company's Emerg Ph #: 501-862-5141

Company's Info Ph #: 317-497-6100

Record No. For Safety Entry: 001

Tot Safety Entries This Stk#: 001

Status: SMJ

Date MSDS Prepared: 01FEB96

Safety Data Review Date: 22JUL97

MSDS Serial Number: CFHNX

Hazard Characteristic Code: NK

===========================================================================

Ingredients/Identity Information

===========================================================================

Proprietary: NO

Ingredient: 1,1,1,2,3,3,3-HEPTAFLUOROPROPANE

Ingredient Sequence Number: 01

Percent: >99

NIOSH (RTECS) Number: 1015387HP

CAS Number: 431-89-0

OSHA PEL: N/K (FP N)

ACGIH TLV: N/K (FP N)

-------------------------------------

Proprietary: NO

Ingredient: SUPDAT:LEVEL (NOAEL) TO BE 9%. LOWEST OBSERVABLE ADVERSE EFT

LEVEL (LOAEL) FOR THIS STUDY WAS RPTD TO BE 10.5%. (ING 3)

Ingredient Sequence Number: 02

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 2:A 90 DAY INHAL STUDY DID NOT FIND ANY EXPOS RELATED EFTS

AT 105,000 PPM (10.5% VOL./VOL.), HIGHEST LEVEL (ING 4)

Ingredient Sequence Number: 03

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 3:TESTED. INHAL STUDIES LOOKING FOR DEVELOPMENTAL EFTS ON

PREGNANT RABBITS & RATS/THEIR OFFSPRING DID NOT (ING 5)

Ingredient Sequence Number: 04

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 4:SHOW ANY EXPOS RELATED EFTS @ HIGHEST CONCS TESTED (105,

000 PPM). SIGNS & SYMPS OF EXPOS:SYMPS SIMILAR TO (ING 6)

Ingredient Sequence Number: 05

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 5:OXYGEN DEPRIVATION (HEADACHE, NAUS, DIZZINESS/LOSS OF

CONSCIOUSNESS) MAY RSLT FROM OVEREXP BY INHAL. HEART(ING 7)

Ingredient Sequence Number: 06

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 6:IRREGULARITIES SUCH AS IRREGULAR PULSE/HEART

PALPITATIONS MAY INDICATE CARDIAC SENSITIVITY. COLD, WHITE/ (ING 8)

Ingredient Sequence Number: 07

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 7:DISCOLORED SKIN/IN SEV CASES BLISTERING, CAN BE SIGN OF

FROSTBITE CAUSED BY COLD LIQ/GASES. FOR DETAILED (ING 9)

Ingredient Sequence Number: 08

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: ING 8:TOXICOLOGICAL STUDY INFORMATION CONTACT NEHC (FP N).

Ingredient Sequence Number: 09

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

-------------------------------------

Proprietary: NO

Ingredient: MED CNDTNS:EXPOSURE TO THESE TYPES OF COMPOUNDS.

Ingredient Sequence Number: 10

NIOSH (RTECS) Number: 9999999ZZ

OSHA PEL: NOT APPLICABLE

ACGIH TLV: NOT APPLICABLE

===========================================================================

Physical/Chemical Characteristics

===========================================================================

Appearance And Odor: COLORLESS GAS, ODORLESS.

Boiling Point: 3F,-16C

Melting Point: -204F,-131C

Vapor Pressure (MM Hg/70 F): 58.8 PSIA

Vapor Density (Air=1): 6.04

Specific Gravity: 1.46 (WATER =1)

Evaporation Rate And Ref: NOT KNOWN

Solubility In Water: 260 MG/L

===========================================================================

Fire and Explosion Hazard Data

===========================================================================

Flash Point: NONFLAMMABLE GAS

Lower Explosive Limit: N/A

Upper Explosive Limit: N/A

Extinguishing Media: ALL CONVENTIONAL MEDIA ARE SUITABLE.

Special Fire Fighting Proc: NIOSH APPRVD SCBA & FULL PROT EQUIP (FP N).

KEEP CYLS COOL W/WATER SPRAY APPLIED FROM SAFE DIST. DO NOT ALLOW REENTRY

INTO AREAS WHERE MATL HAS BEEN (SUPDAT)

Unusual Fire And Expl Hazrds: ALTHOUGH CNTNRS OF PROD ARE PROVIDED W/PRESS

& TEMP RELIEF DEVICES, CNTNRS CAN RUPTURE IF EXPOS TO LOCALIZED HEAT. THERM

DECOMP WILL GENERATE TOXIC & (SUPDAT)

===========================================================================

Reactivity Data

===========================================================================

Stability: YES

Cond To Avoid (Stability): NONE KNOWN.

Materials To Avoid: POWDERED METALS (EX. AL, MG/ZN) & STRONG ALKALIS,

OXIDIZERS/REDUCING AGENTS ARE NOT COMPAT W/THIS & MOST OTHER (SUPDAT)

Hazardous Decomp Products: DECOMP BY ELEVATED TEMPS (FIRE CNDTNS, GLOWING

METAL SURF) MAY GENERATE HAZ DECOMP PRODS COMMON TO OTHER CFCS, (SUPDAT)

Hazardous Poly Occur: NO

Conditions To Avoid (Poly): NOT RELEVANT.

===========================================================================

Health Hazard Data

===========================================================================

LD50-LC50 Mixture: NONE SPECIFIED BY MANUFACTURER.

Route Of Entry - Inhalation: YES

Route Of Entry - Skin: NO

Route Of Entry - Ingestion: NO

Health Haz Acute And Chronic: ACUTE:HUMAN HLTH HAZ OF PROD ARE EXPECTED TO

BE SIMILAR TO OTHER LIQUIFIED GASES INCL N*2, CO*2, CFCS, HCFCS, & HBFCS.

THEREFORE, DIRECT EYE/SKIN CONT W/LIQ OR COLD GAS CAN CAUSE CHILLING/

POSSIBLY FROSTBITE OF EXPOS TISS. INHAL OF HIGH CONCS CAN BE HARMFUL/FATAL

DUE TO OXYG DEPRIVATION AND/OR HEART (EFTS OF OVEREXP)

Carcinogenicity - NTP: NO

Carcinogenicity - IARC: NO

Carcinogenicity - OSHA: NO

Explanation Carcinogenicity: NOT RELEVANT.

Signs/Symptoms Of Overexp: HLTH HAZ:IRREGULARITIES (ARRHY). MISUSE OF PROD

BY DELIBERATELY INHALING HIGH CONCS OF GAS COULD CAUSE DEATH W/OUT WARNING.

PERSONS W/PREEXISTING CARD/CNS DISORDERS MAY BE MORE SUSCEPTIBLE TO EFTS OF

OVEREXP. ANIMAL STUDIES HAVE FOUND RAT 4 HR LC50 TO BE >788,696 PPM ( 80%),

HIGHEST LEVEL TESTED. CARD SENSIT (SUPDAT)

Med Cond Aggravated By Exp: PERSONS W/PREEXISTING CARD, RESP/CNS DISORDERS

MAY BE MORE SUSCEPTIBLE TO EFTS OF OVEREXP. USE OF EPINEPHRINE/ SIMILAR

CMPDS CAN INCR SUSCEPTIBILITY TO HEART IRREGULARITIES CAUSED BY EXCESS (ING10)

Emergency/First Aid Proc: INGEST:CALL MD IMMEDIATELY (FP N). INHAL: REMOVE

TO FRESH AIR; GIVE ARTIFICIAL RESPIRATION. IF BRTHG IS DIFFICULT, GIVE

OXYGEN. GET MEDICAL ATTENTION. SKIN:FLUSH WITH WATER; IF FROSTBITE OCCURS,

GET MEDICAL ATTENTION. EYES:FLUSH WITH WATER FOR AT LEAST 15 MINUTES. GET

MEDICAL ATTENTION.

===========================================================================

Precautions for Safe Handling and Use

===========================================================================

Steps If Matl Released/Spill: EVAC AREA & VENTILATE. DO NOT ENTER AREAS

WHERE HIGH CONCS MAY EXIST (ESPECIALLY CONFINED/POORLY VENTILATED AREAS) W/

OUT APPROP PROT EQUIP INCLUDING NIOSH APPRVD SELF-CONTAINED BREATHING APPARATUS.

Neutralizing Agent: NONE SPECIFIED BY MANUFACTURER.

Waste Disposal Method: NON-CONTAMD PROD IS RECLAIMABLE. CONT GREAT LAKES

CHEM CORP FOR INFO. OTHERWISE, DISPOSE OF WASTE IN APPRVD CHEM INCIN

EQUIPPED W/SCRUBBER AS ALLOWED BY CURRENT LOCAL, STATE/PROVINCE, FED/

CANADIAN LAWS & REGULATIONS.

Precautions-Handling/Storing: USE SAME TYPE OF PRECAUTIONS AS WOULD BE

USED IN HNDLG ANY CRYOGENIC GAS. PROTECT CNTNR FROM DAMAGE. HANDLE IN WELL-

VENTILATED AREAS.

Other Precautions: WHEN THIS MATL IS USED AS FIRE FIGHTING AGENT IN FIXED

OR PORTABLE EXTINGUISHING SYSTEMS, FOLLOW MFR'S INSTRUCTIONS FOR OPERATION,

INSPECTION, MAINTENANCE & REPAIR OF THE SYSTEM.

===========================================================================

Control Measures

===========================================================================

Respiratory Protection: WEAR A NIOSH APPROVED SELF-CONTAINED BREATHING

APPARATUS IN EMERGENCY SITUATIONS.

Ventilation: LOCAL EXHAUST-USE TO MINIMIZE EXPOSURE TO GAS. MECHANICAL-USE

FOR GENERAL AREA CONTROL.

Protective Gloves: LINED NEOPRENE GLOVES.

Eye Protection: ANSI APPRVD CHEM WORKERS GOGGLES (FP N).

Other Protective Equipment: ANSI APPRVD EYE WASH & DELUGE SHOWER (FP N).

Work Hygienic Practices: ENSURE PIPING IS EMPTY BEFORE DOING MAINTENANCE WORK.

Suppl. Safety & Health Data: FIRE FIGHT PROC:RELEASED W/OUT FIRST

VENTILATING TO REMOVE PRODS OF COMBUST/DECOMP. EXPLO HAZ:CORR GASES. MATLS

TO AVOID:HALOGENATED ORG CMPDS. HAZ DECOMP PROD:HCFCS/HBFCS. THESE CAN INCL

HYDROGEN FLUORIDE, CARBON MONOXIDE, CARBON DIOXIDE & OTHERS. EFTS OF

OVEREXP:STUDY IN DOGS FOUND NO OBSERVABLE ADVERSE EFT (ING 2)

===========================================================================

Transportation Data

===========================================================================

===========================================================================

Disposal Data

===========================================================================

===========================================================================

Label Data

===========================================================================

Label Required: YES

Technical Review Date: 22JUL97

Label Date: 22JUL97

Label Status: G

Common Name: 1,1,1,2,3,3,3-HEPTAFLUOROPROPANE, FM-200

Chronic Hazard: NO

Signal Word: WARNING!

Acute Health Hazard-Moderate: X

Contact Hazard-Moderate: X

Fire Hazard-None: X

Reactivity Hazard-None: X

Special Hazard Precautions: ACUTE:DIRECT CONTACT WITH LIQUID OR COLD GAS

CAN CAUSE CHILLING OR POSSIBLY FROSTBITE OF EXPOSED TISSUE. ASPHYXIANT-

SYMPTOMS INCLUDE HEADACHE, NAUSEA, DIZZINESS AND UNCONSCIOUSNESS. IRREGULAR

HEARTBEATS MAY ALSO OCCUR. CHRONIC:NONE LISTED BY MANUFACTURER.

Protect Eye: Y

Protect Skin: Y

Protect Respiratory: Y

Label Name: GREAT LAKES CHEMICAL CORP

Label Street: ONE GREAT LAKES BLVD

Label P.O. Box: 2200

Label City: WEST LAFAYETTE

Label State: IN

Label Zip Code: 47906

Label Country: US

Label Emergency Number: 501-862-5141